## Matrix+Cover Sheet
Likelihood of Failure
|  |  |  | Imminent | Probable | Possible | Improbable | No Potential
|  |  |  | 20 | 15 | 10 | 5 | 0
Consequence of Failure
|  |  |  | Severe Close to waterway High volume | Close to waterway Low-Moderate Volume | Far from Waterway Moderate Volume | Minimal Far from Waterway Low Volume | None
|  |  |  | 20 | 15 | 10 | 5 | 0
Hydraulic Capacity / O&M Ability
|  |  |  | Very Poor Low Capacity Frequent Hotspot | Poor Tuberculated pipe | Fair | Good | New No Capacity Issues Not a hotspot
|  |  |  | 20 | 15 | 10 | 5 | 0
Asset Condition
|  |  |  | Very Poor Broken or deformed pipe, Root balls, High I&I, ACP/CIP/DIP | Poor Fractures Mod-Tap roots Some I&I | Fair Cracks Light roots Light I&I | Good Minimal roots or cracks | New
|  |  |  | 20 | 15 | 10 | 5 | 0
Time Criticality
|  |  |  | 1 year or less | 1 to 3 years | 3 to 5 years | More than 5 years | Not time critical
|  |  |  | 20 | 15 | 10 | 5 | 0
Constructability
|  |  |  | Design Complete | In Design | Scope Complete | Conceptual Design Needed | Scope Unknown
|  |  |  | 20 | 15 | 10 | 5 | 0
System Impact / Redundancy
|  |  |  | Critical lone system | Active redundancy | Passive redundancy | Fault-tolerant, no alarm | Fault tolerant, with alarm
|  |  |  | 20 | 15 | 10 | 5 | 0
Regulatory / Compliance Risk
|  |  |  | Out of Compliance |  |  |  | No Potential
|  |  |  | 20 | 15 | 10 | 5 | 0
Public Health and Safety
|  |  |  | Ongoing risk |  |  |  | No risk
|  |  |  | 20 | 15 | 10 | 5 | 0
| Bold font indicates project is recommended for FY26-27 budget | Cost Estimate | Risk Category: | Likelihood of Failure | Consequence of Failure | Hydraulic Capacity / O&M Ability | Asset Condition | Time Criticality | Constructability | Risk-Probability Value
|  |  | Max Value: | 20 | 20 | 20 | 20 | 20 | 20
|  |  | Weight: | 30% | 30% | 15% | 15% | 5% | 5%
Large-Scale CIP: Trunk | Former MO Trunk Improvements-Design | 150000 |  | 20 | 20 | 10 | 20 | 15 | 5 | 87.5
| Former MO Trunk Improvements-Construction | 2500000 |  | 20 | 20 | 10 | 20 | 15 | 5 | 87.5
| Techite Pipe Rehabilitation | 560000 |  | 18 | 20 | 10 | 15 | 20 | 15 | 84.5
| Old Creek Rd Rehab | 1240000 |  | 12 | 20 | 5 | 15 | 15 | 10 | 69.25
| Ojai Asbestos Pipe Rehab. | 530000 |  | 15 | 20 | 5 | 15 | 15 | 10 | 73.75
| Prospect Trunk Sewer Realignment | 820000 |  | 5 | 20 | 15 | 15 | 5 | 5 | 62.5
| Foster Park Sewer Relocation | 5060000 |  | 10 | 20 | 10 | 10 | 5 | 0 | 61.25
| San Antonio Creek Siphon | 2020000 |  | 10 | 20 | 10 | 5 | 5 | 0 | 57.5
| Creek Road Siphons (4) | 5890000 |  | 10 | 20 | 10 | 5 | 5 | 0 | 57.5
| Cast Iron and Ductile Iron Pipe Rehabilitation-Trunk | 1175000 |  | 15 | 20 | 15 | 20 | 5 | 5 | 81.25
Future Project
| Future Project | [8 empty] | 0
Large-Scale CIP: Collectors | Pipe Bursting - Rancho Dr | 580000 |  | 20 | 15 | 15 | 15 | 20 | 15 | 83.75
| Pipe Bursting - Alto Dr | 710000 |  | 20 | 10 | 10 | 10 | 15 | 15 | 67.5
| Pipe Bursting - Feliz Dr | 190000 |  | 15 | 10 | 15 | 15 | 15 | 10 | 66.25
| N. Ventura Ave. Improvements | 3150000 |  | 15 | 20 | 20 | 10 | 15 | 5 | 80
| Barbara St. O&M Improvements | 210000 |  | 0 | 15 | 20 | 10 | 10 | 10 | 50
| Mira Monte Sewer Improvements | 400000 |  | 20 | 10 | 20 | 20 | 10 | 0 | 77.5
| Lomita Ave Sewer Improvements | 330000 |  | 5 | 15 | 20 | 10 | 5 | 10 | 56.25
| Pirie Road Sewer Improvements | 360000 |  | 5 | 10 | 20 | 10 | 5 | 10 | 48.75
| Meiners Oaks (BO1) Sewer Main Rehab. and Pipe Bursting | 17050000 |  | 20 | 12 | 18 | 10 | 5 | 5 | 71.5
| Oak View (CO2, CO5, CO6) Sewer Main Rehab. and Pipe Bursting | 20880000 |  | 20 | 12 | 18 | 10 | 5 | 5 | 71.5
| Cast Iron and Ductile Iron Pipe Rehabilitation-Collectors | 638000 |  | 15 | 15 | 15 | 20 | 5 | 5 | 73.75
Future Project
| Future Project | [8 empty] | 0
Large-Scale CIP: Lift Stations | Santa Ana Lift Station No. 2 Improvements | 820000 |  | 10 | 20 | 15 | 10 | 5 | 15 | 68.75
| RMLS Lift Station Improvements | 150000 |  | 20 | 20 | 15 | 10 | 20 | 20 | 88.75
| OLS Lift Station Improvements | 25000 |  | 15 | 20 | 15 | 10 | 15 | 20 | 80
Misc. Improvements | E-One Pump Test Area (at WWTP) | 138000 | [7 empty] | 0
| Septage Receiving System | 354000 | [7 empty] | 0
0
Studies | I&I Study: Upstream of Prospect Meter | 75000 | [7 empty] | 0
| Easement Acquisition and/or Abandonment | 1000000 | [7 empty] | 0
0
Admin | Tico ADA Compliance | 225000 | [7 empty] | 0
| Break Room, Board Room Improvements | [8 empty] | 0
| Locker Rooms + Eng. / IT Improvements | [8 empty] | 0

## Techite
Cover Sheet | The scope of this project is directly from 2011 CIP |  |  |  |  | Techite Pipe + 1 Upstream VCP
Item | Description - Techite Pipe Rehab (OVT near Grande Vista) G-20-05 to G-19-06 | Cost |  |  |  | 8in | 10in | 12in | 15in | 18in | 21in | 24in | Enter Values for Yellow Cells
1.01 | Design | 24000 |  | Small, simple design @ 5% | Length: | 0 | 0 | 0 | 966 | 740 | 0 | 0 |  | 8in | 10in | 12in | 15in | 18in | 21in | 24in
1.02 | Environmental Design | 0 |  |  | CCTV: | 0 | 0 | 0 | 11592 | 11100 | 0 | 0 | Rehab. Cost per Ft 2025 Estimate | 50 | 60 | 100 | 200 | 225 | 250 | 300
2.01 | Temporary and/or Permanent Easements | 0 |  | No easements anticipated | Rehab: | 0 | 0 | 0 | 193200 | 166500 | 0 | 0 | CCTV/Prep Cost per Ft 2025 Estimate | 10 | 10 | 10 | 12 | 15 | 15 | 20
2.02 | Permits (ROW, VCWPD, 401, 404, etc.) | 1000 |  | Assume each project is $1M and needs a $2,500 permit | [8 empty] | Avg prop line (dense) | 75
3.01 | Construction Management | 24000 |  | CM assistance at 5% | No. MHs: | 6 | [6 empty] | Avg prop line (rural) | 200
3.02 | Construction Phase Services | 12000 |  | CPS at 2.% | Rehab Cost / MH inc. TC: | 7500 | [6 empty] | Sewer Lateral Re-establishment | 1500
3.03 | Inspection | 17000 |  | Contract inspection | [8 empty] | Sewer Lateral Insert | 4000
3.04 | Material Testing | 0 |  | No paving, MH testing included in price | [8 empty] | Traffic Control / Day (Minor) | 1500
4.01 | Restoration | 0 |  | No restoration anticipated. | [8 empty] | Traffic Control / Day (Significant) | 3000
4.02 | Mitigation | 0 |  | No mitigation anticipated | [8 empty] | Traffic Control / Day (Caltrans) | 3500
5.01 | Mobilization | 23000 | [10 empty] | Point Repair Est. | 10000
5.02 | Traffic Control (reduced to half minor TC cost) | 10000 | [10 empty] | Inspection / Day | 1760
5.03 | Point Repairs | 17000
5.04 | CCTV Inspection and Pipe Preparation | 23000
5.05 | Sewer Main Lining | 360000
5.06 | Sewer Lateral Re-Establishment / Lateral Inserts | 0 |  | None
5.07 | Manhole Rehabilitation | 45000
6.01 | Closeout, As-builts | 4000
| TOTAL | 560000 | 0
| Design and Environmental | 25000
| Inspection and Construction Management | 53000
| Construction and Closeout | 482000
| Total Cost | 560000

## 2026 Pipe Bursting-v1
Cover Sheet
Item | Description - Rancho Dr and Alto/Feliz Dr Pipe Bursting | Cost |  | Comments / Assumptions | [9 empty] | Enter Values for Yellow Cells
1.01 | Design | 89000 |  | Small, simple design @ 7.5% |  | 6in | 8in | 10in | 12in | 15in | 18in | 21in | 24in |  | 6in | 8in | 10in | 12in | 15in | 18in | 21in | 24in
1.02 | Environmental Design | 0 |  | Anticipate need for arborist report ($50k + $50k over time) | Length: | 3810 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rehab. Cost per Ft 2025 Estimate | 75 | 50 | 60 | 100 | 200 | 225 | 250 | 300
2.01 | Temporary and/or Permanent Easements | 0 |  | No easements anticipated | CCTV: | 57150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bursting Cost per Ft Estimate | 275 | 275 | 300 | 325 | 350 | 450 | 500 | 600
2.02 | Permits (ROW, VCWPD, 401, 404, etc.) | 3000 |  | Assume each project is $1M and needs a $2,500 permit | Rehab (Lining): | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CCTV/Prep Cost per Ft 2025 Estimate | 15 | 10 | 10 | 10 | 12 | 15 | 15 | 20
3.01 | Construction Management | 60000 |  | CM assistance at 5% | Bursting: | 1047750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Avg prop line (dense) | 75
3.02 | Construction Phase Services | 60000 |  | CPS at 5% | [9 empty] | Avg prop line (rural) | 200
3.03 | Inspection | 50000 |  | Contract inspection | [9 empty] | Sewer Lateral Re-establishment | 1500
3.04 | Material Testing | 8000 |  | Testing for final A/C paving in bursting area |  | 3810 | [7 empty] | Sewer Lateral Insert | 4000
4.01 | Restoration | 0 |  | Restoration embedded in constructon. No major restoration projects anticipated. | [9 empty] | Traffic Control / Day (Minor) | 1500
4.02 | Mitigation | 0 |  | No mitigation anticipated | [9 empty] | Traffic Control / Day (Significant) | 3000
5.01 | Mobilization | 57000 |  | Note: this will be separate D&C projects over many years | [9 empty] | Traffic Control / Day (Caltrans) | 3500
5.02 | Traffic Control | 29000 |  | TC complex in MO. 400 LF/day CIPP, 150 LF/day bursting. | [9 empty] | Point Repair Est. | 10000
5.03 | Point Repairs | 0 |  | High GW in MO per 2014 I&I study. May be required in CIPP and bursting area. | [9 empty] | Point Repair High GW | 15000
5.04 | CCTV Inspection and Pipe Preparation | 57000 | [11 empty] | Inspection / Day | 1760
5.05 | Sewer Main Lining (>6in) | 0
5.06 | Sewer Main Bursting (6in) inc. Lateral Connection | 1048000 |  | Note: may be more practical to open trench due to short P/Ls in MO
5.07 | Sewer Lateral Re-Establishment (CIPP only) | 0
5.08 | Sewer Lateral Insert (CIPP only) | 0
6.1 | Closeout, As-builts | 7000
| TOTAL | 1470000 | 0
| Design and Environmental | 92000
| Inspection and Construction Management | 170000
| Construction and Closeout | 1206000
| Total Cost | 1468000
1

## 2026 PB-Rancho Only
Cover Sheet
Item | Description - Rancho Dr Pipe Bursting | Cost |  | Comments / Assumptions | [9 empty] | Enter Values for Yellow Cells
1.01 | Design | 35000 |  | Small, simple design @ 7.5% |  | 6in | 8in | 10in | 12in | 15in | 18in | 21in | 24in |  | 6in | 8in | 10in | 12in | 15in | 18in | 21in | 24in
1.02 | Environmental Design | 0 |  | Anticipate need for arborist report ($50k + $50k over time) | Length: | 1490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rehab. Cost per Ft 2025 Estimate | 75 | 50 | 60 | 100 | 200 | 225 | 250 | 300
2.01 | Temporary and/or Permanent Easements | 0 |  | No easements anticipated | CCTV: | 22350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bursting Cost per Ft Estimate | 275 | 275 | 300 | 325 | 350 | 450 | 500 | 600
2.02 | Permits (ROW, VCWPD, 401, 404, etc.) | 1000 |  | Assume each project is $1M and needs a $2,500 permit | Rehab (Lining): | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CCTV/Prep Cost per Ft 2025 Estimate | 15 | 10 | 10 | 10 | 12 | 15 | 15 | 20
3.01 | Construction Management | 23000 |  | CM assistance at 5% | Bursting: | 409750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Avg prop line (dense) | 75
3.02 | Construction Phase Services | 23000 |  | CPS at 5% | [9 empty] | Avg prop line (rural) | 200
3.03 | Inspection | 20000 |  | Contract inspection | [9 empty] | Sewer Lateral Re-establishment | 1500
3.04 | Material Testing | 3000 |  | Testing for final A/C paving in bursting area |  | 1490 | [7 empty] | Sewer Lateral Insert | 4000
4.01 | Restoration | 0 |  | Restoration embedded in constructon. No major restoration projects anticipated. | [9 empty] | Traffic Control / Day (Minor) | 1500
4.02 | Mitigation | 0 |  | No mitigation anticipated | [9 empty] | Traffic Control / Day (Significant) | 3000
5.01 | Mobilization | 22000 |  | Note: this will be separate D&C projects over many years | [9 empty] | Traffic Control / Day (Caltrans) | 3500
5.02 | Traffic Control | 11000 |  | TC complex in MO. 400 LF/day CIPP, 150 LF/day bursting. | [9 empty] | Point Repair Est. | 10000
5.03 | Point Repairs | 0 |  | High GW in MO per 2014 I&I study. May be required in CIPP and bursting area. | [9 empty] | Point Repair High GW | 15000
5.04 | CCTV Inspection and Pipe Preparation | 22000 | [11 empty] | Inspection / Day | 1760
5.05 | Sewer Main Lining (>6in) | 0
5.06 | Sewer Main Bursting (6in) inc. Lateral Connection | 410000 |  | Note: may be more practical to open trench due to short P/Ls in MO
5.07 | Sewer Lateral Re-Establishment (CIPP only) | 0
5.08 | Sewer Lateral Insert (CIPP only) | 0
6.1 | Closeout, As-builts | 3000
| TOTAL | 580000 | 0
| Design and Environmental | 36000
| Inspection and Construction Management | 66000
| Construction and Closeout | 471000
| Total Cost | 573000
1

## 2026 PB-Alto Only
Cover Sheet
Item | Description - Alto Dr Pipe Bursting | Cost |  | Comments / Assumptions | [9 empty] | Enter Values for Yellow Cells
1.01 | Design | 43000 |  | Small, simple design @ 7.5% |  | 6in | 8in | 10in | 12in | 15in | 18in | 21in | 24in |  | 6in | 8in | 10in | 12in | 15in | 18in | 21in | 24in
1.02 | Environmental Design | 0 |  | Anticipate need for arborist report ($50k + $50k over time) | Length: | 1830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rehab. Cost per Ft 2025 Estimate | 75 | 50 | 60 | 100 | 200 | 225 | 250 | 300
2.01 | Temporary and/or Permanent Easements | 0 |  | No easements anticipated | CCTV: | 27450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bursting Cost per Ft Estimate | 275 | 275 | 300 | 325 | 350 | 450 | 500 | 600
2.02 | Permits (ROW, VCWPD, 401, 404, etc.) | 1000 |  | Assume each project is $1M and needs a $2,500 permit | Rehab (Lining): | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CCTV/Prep Cost per Ft 2025 Estimate | 15 | 10 | 10 | 10 | 12 | 15 | 15 | 20
3.01 | Construction Management | 29000 |  | CM assistance at 5% | Bursting: | 503250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Avg prop line (dense) | 75
3.02 | Construction Phase Services | 29000 |  | CPS at 5% | [9 empty] | Avg prop line (rural) | 200
3.03 | Inspection | 24000 |  | Contract inspection | [9 empty] | Sewer Lateral Re-establishment | 1500
3.04 | Material Testing | 4000 |  | Testing for final A/C paving in bursting area |  | 1830 | [7 empty] | Sewer Lateral Insert | 4000
4.01 | Restoration | 0 |  | Restoration embedded in constructon. No major restoration projects anticipated. | [9 empty] | Traffic Control / Day (Minor) | 1500
4.02 | Mitigation | 0 |  | No mitigation anticipated | [9 empty] | Traffic Control / Day (Significant) | 3000
5.01 | Mobilization | 27000 |  | Note: this will be separate D&C projects over many years | [9 empty] | Traffic Control / Day (Caltrans) | 3500
5.02 | Traffic Control | 14000 |  | TC complex in MO. 400 LF/day CIPP, 150 LF/day bursting. | [9 empty] | Point Repair Est. | 10000
5.03 | Point Repairs | 0 |  | High GW in MO per 2014 I&I study. May be required in CIPP and bursting area. | [9 empty] | Point Repair High GW | 15000
5.04 | CCTV Inspection and Pipe Preparation | 27000 | [11 empty] | Inspection / Day | 1760
5.05 | Sewer Main Lining (>6in) | 0
5.06 | Sewer Main Bursting (6in) inc. Lateral Connection | 503000 |  | Note: may be more practical to open trench due to short P/Ls in MO
5.07 | Sewer Lateral Re-Establishment (CIPP only) | 0
5.08 | Sewer Lateral Insert (CIPP only) | 0
6.1 | Closeout, As-builts | 3000
| TOTAL | 710000 | 0
| Design and Environmental | 44000
| Inspection and Construction Management | 82000
| Construction and Closeout | 578000
| Total Cost | 704000
1

## 2026 PB-Feliz Only
Cover Sheet
Item | Description - Feliz Dr Pipe Bursting | Cost |  | Comments / Assumptions | [9 empty] | Enter Values for Yellow Cells
1.01 | Design | 11000 |  | Small, simple design @ 7.5% |  | 6in | 8in | 10in | 12in | 15in | 18in | 21in | 24in |  | 6in | 8in | 10in | 12in | 15in | 18in | 21in | 24in
1.02 | Environmental Design | 0 |  | Anticipate need for arborist report ($50k + $50k over time) | Length: | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rehab. Cost per Ft 2025 Estimate | 75 | 50 | 60 | 100 | 200 | 225 | 250 | 300
2.01 | Temporary and/or Permanent Easements | 0 |  | No easements anticipated | CCTV: | 7350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bursting Cost per Ft Estimate | 275 | 275 | 300 | 325 | 350 | 450 | 500 | 600
2.02 | Permits (ROW, VCWPD, 401, 404, etc.) | 0 |  | Assume each project is $1M and needs a $2,500 permit | Rehab (Lining): | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CCTV/Prep Cost per Ft 2025 Estimate | 15 | 10 | 10 | 10 | 12 | 15 | 15 | 20
3.01 | Construction Management | 8000 |  | CM assistance at 5% | Bursting: | 134750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Avg prop line (dense) | 75
3.02 | Construction Phase Services | 8000 |  | CPS at 5% | [9 empty] | Avg prop line (rural) | 200
3.03 | Inspection | 6000 |  | Contract inspection | [9 empty] | Sewer Lateral Re-establishment | 1500
3.04 | Material Testing | 1000 |  | Testing for final A/C paving in bursting area |  | 490 | [7 empty] | Sewer Lateral Insert | 4000
4.01 | Restoration | 0 |  | Restoration embedded in constructon. No major restoration projects anticipated. | [9 empty] | Traffic Control / Day (Minor) | 1500
4.02 | Mitigation | 0 |  | No mitigation anticipated | [9 empty] | Traffic Control / Day (Significant) | 3000
5.01 | Mobilization | 7000 |  | Note: this will be separate D&C projects over many years | [9 empty] | Traffic Control / Day (Caltrans) | 3500
5.02 | Traffic Control | 4000 |  | TC complex in MO. 400 LF/day CIPP, 150 LF/day bursting. | [9 empty] | Point Repair Est. | 10000
5.03 | Point Repairs | 0 |  | High GW in MO per 2014 I&I study. May be required in CIPP and bursting area. | [9 empty] | Point Repair High GW | 15000
5.04 | CCTV Inspection and Pipe Preparation | 7000 | [11 empty] | Inspection / Day | 1760
5.05 | Sewer Main Lining (>6in) | 0
5.06 | Sewer Main Bursting (6in) inc. Lateral Connection | 135000 |  | Note: may be more practical to open trench due to short P/Ls in MO
5.07 | Sewer Lateral Re-Establishment (CIPP only) | 0
5.08 | Sewer Lateral Insert (CIPP only) | 0
6.1 | Closeout, As-builts | 1000
| TOTAL | 190000 | 0
| Design and Environmental | 11000
| Inspection and Construction Management | 22000
| Construction and Closeout | 155000
| Total Cost | 188000
1

## OCR Rehab
Cover Sheet | Old Creek Road to GSC
Item | Description - Trunk Sewer Rehab. (Old Creek Rd I-19-02 to H-18-08) | Cost |  |  |  | 8in | 10in | 12in | 15in | 18in | 21in | 24in | Enter Values for Yellow Cells
1.01 | Design | 73000 |  | Small, simple design @ 7.5% | Length: | 0 | 0 | 0 | 0 | 0 | 2480 | 0 |  | 8in | 10in | 12in | 15in | 18in | 21in | 24in
1.02 | Environmental Design | 0 |  |  | CCTV: | 0 | 0 | 0 | 0 | 0 | 37200 | 0 | Rehab. Cost per Ft 2025 Estimate | 50 | 60 | 100 | 200 | 225 | 250 | 300
2.01 | Temporary and/or Permanent Easements | 0 |  | No easements anticipated | Rehab: | 0 | 0 | 0 | 0 | 0 | 620000 | 0 | CCTV/Prep Cost per Ft 2025 Estimate | 10 | 10 | 10 | 12 | 15 | 15 | 20
2.02 | Permits (ROW, VCWPD, 401, 404, etc.) | 2000 |  | Assume each project is $1M and needs a $2,500 permit | [8 empty] | Avg prop line (dense) | 75
3.01 | Construction Management | 98000 |  | CM assistance at 10% | [8 empty] | Avg prop line (rural) | 200
3.02 | Construction Phase Services | 49000 |  | CPS at 5% | [8 empty] | Sewer Lateral Re-establishment | 1500
3.03 | Inspection | 33000 |  | Contract inspection | [8 empty] | Sewer Lateral Insert | 4000
3.04 | Material Testing | 0 |  | No paving | [8 empty] | Traffic Control / Day (Minor) | 1500
4.01 | Restoration | 0 |  | No restoration anticipated. | [8 empty] | Traffic Control / Day (Significant) | 3000
4.02 | Mitigation | 0 |  | No mitigation anticipated | [8 empty] | Traffic Control / Day (Caltrans) | 3500
5.01 | Mobilization | 47000 | [10 empty] | Point Repair Est. | 10000
5.02 | Traffic Control | 56000 | [10 empty] | Point Repair High GW | 15000
5.03 | Point Repairs | 37000 | [10 empty] | Inspection / Day | 1760
5.04 | CCTV Inspection and Pipe Preparation | 37000
5.05 | Sewer Main Lining | 620000
5.06 | Sewer Lateral Re-Establishment | 50000
5.07 | Sewer Lateral Insert | 132000
6.01 | Closeout, As-builts | 5000
| TOTAL | 1240000 | 0
| TOTAL 2--In-house Design | 1031000
| Design and Environmental | 75000
| Inspection and Construction Management | 180000
| Construction and Closeout | 984000
| Total Cost | 1239000

## Ojai ACP Rehab
Cover Sheet | City: ACP Golden West to Shady Ln
Item | Description - Trunk Sewer Rehab. (Ojai Trunk from S-30-07 to S-30-16) | Cost |  |  |  | 8in | 10in | 12in | 15in | 18in | 21in | 24in | Enter Values for Yellow Cells
1.01 | Design | 39000 |  | Small CalTrans design @ 10% | Length: | 0 | 0 | 0 | 1085 | 0 | 0 | 0 |  | 8in | 10in | 12in | 15in | 18in | 21in | 24in
1.02 | Environmental Design | 0 |  |  | CCTV: | 0 | 0 | 0 | 13020 | 0 | 0 | 0 | Rehab. Cost per Ft 2025 Estimate | 50 | 60 | 100 | 200 | 225 | 250 | 300
2.01 | Temporary and/or Permanent Easements | 0 |  | No easements anticipated | Rehab: | 0 | 0 | 0 | 217000 | 0 | 0 | 0 | CCTV/Prep Cost per Ft 2025 Estimate | 10 | 10 | 10 | 12 | 15 | 15 | 20
2.02 | Permits (ROW, VCWPD, 401, 404, etc.) | 5000 | [10 empty] | Avg prop line (dense) | 75
3.01 | Construction Management | 39000 |  | CM assistance at 10% | [8 empty] | Avg prop line (rural) | 200
3.02 | Construction Phase Services | 29000 |  | CPS at 7.5% | [8 empty] | Sewer Lateral Re-establishment | 1500
3.03 | Inspection | 19000 |  | Contract inspection | [8 empty] | Sewer Lateral Insert | 4000
3.04 | Material Testing | 0 |  | No paving | [8 empty] | Traffic Control / Day (Minor) | 1500
4.01 | Restoration | 0 |  | No restoration anticipated. | [8 empty] | Traffic Control / Day (Significant) | 3000
4.02 | Mitigation | 0 |  | No mitigation anticipated | [8 empty] | Traffic Control / Day (Caltrans) | 3500
5.01 | Mobilization | 19000 | [10 empty] | Point Repair Est. | 10000
5.02 | Traffic Control | 57000 | [10 empty] | Point Repair High GW or Complex | 15000
5.03 | Point Repairs | 54000 |  | High GW/Complex | [8 empty] | Inspection / Day | 1760
5.04 | CCTV Inspection and Pipe Preparation | 13000
5.05 | Sewer Main Lining | 217000
5.06 | Sewer Lateral Re-Establishment | 8000
5.07 | Sewer Lateral Insert | 22000
6.01 | Closeout, As-builts | 3000
| TOTAL | 530000 | 0
| Design and Environmental | 44000
| Inspection and Construction Management | 87000
| Construction and Closeout | 393000
| Total Cost | 524000

## N.Vent Ave Improv.
Cover Sheet | "Restaurant Row"
Item | Description - N. Ventura Ave. Sewer Improvements | Cost |  | Comments / Assumptions | [9 empty] | Enter Values for Yellow Cells
1.01 | Design | 240000 |  | Small, simple design @ 7.5% |  | 6in | 8in | 10in | 12in | 15in | 18in | 21in | 24in |  | 6in | 8in | 10in | 12in | 15in | 18in | 21in | 24in
1.02 | Environmental Design | 25000 |  | Anticipate need for arborist report ($15k + $10k over time) | Length: | 286 | 3212 | 0 | 0 | 0 | 0 | 0 | 0 | Rehab. Cost per Ft 2025 Estimate | 75 | 50 | 60 | 100 | 200 | 225 | 250 | 300
2.01 | Temporary and/or Permanent Easements | 0 |  | No easements anticipated | CCTV: | 4290 | 32120 | 0 | 0 | 0 | 0 | 0 | 0 | Bursting Cost per Ft Estimate | 275 | 275 | 300 | 325 | 350 | 450 | 500 | 600
2.02 | Permits (ROW, VCWPD, 401, 404, etc.) | 10000 |  | Caltrans | Rehab (Lining): | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Dig and Replce per Ft Estimate | 450 | 500 | 550 | 600 | 700 | 800 | 1000 | 1250
3.01 | Construction Management | 120000 |  | CM assistance at 5% | Bursting: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CCTV/Prep Cost per Ft 2025 Estimate | 15 | 10 | 10 | 10 | 12 | 15 | 15 | 20
3.02 | Construction Phase Services | 120000 |  | CPS at 5% | Dig and Replace | 128700 | 1606000 | 0 | 0 | 0 | 0 | 0 | 0 | Avg prop line (dense) | 75
3.03 | Inspection | 185000 |  | Contract inspection | [9 empty] | Avg prop line (rural) | 200
3.04 | Material Testing | 28000 |  | Testing for final A/C paving |  | 3498 | [7 empty] | Sewer Lateral Re-establishment | 1500
4.01 | Restoration | 0 |  | Restoration embedded in constructon. No major restoration projects anticipated. | [9 empty] | Sewer Lateral Insert | 4000
4.02 | Mitigation | 0 |  | No mitigation anticipated | [9 empty] | Traffic Control / Day (Minor) | 1500
5.01 | Mobilization | 114000 | [11 empty] | Traffic Control / Day (Significant) | 3000
5.02 | Traffic Control | 163000 |  | Caltrans TC | [9 empty] | Traffic Control / Day (Caltrans) | 3500
5.03 | Point Repairs | 0 |  | High GW in MO per 2014 I&I study. May be required in CIPP and bursting area. | [9 empty] | Point Repair Est. | 10000
5.04 | CCTV Inspection and Pipe Preparation | 36000 | [11 empty] | Point Repair High GW | 15000
5.05 | Sewer Main Lining (>6in) | 0 | [11 empty] | Inspection / Day | 1760
5.06 | Sewer Main Bursting (6in) inc. Lateral Connection | 0 |  | Note: may be more practical to open trench due to short P/Ls in MO
5.07 | Sewer Main Replacement | 2082000 |  | +20% Caltrans
5.08 | Sewer Lateral Re-Establishment (CIPP only) | 0
5.09 | Sewer Lateral Insert (CIPP only) | 0
6.1 | Closeout, As-builts | 18000
| TOTAL | 3150000 | 0
| Design and Environmental | 275000
| Inspection and Construction Management | 425000
| Construction and Closeout | 2441000
| Total Cost | 3141000
| Conceptual Design | 120000
| Final Design | 163000
| Construction inc CM, Insp | 2858000
1 | Total Cost | 3141000

## Barbara St MHs
Cover Sheet | Barbara & Calle Vista del Monte x Puesta del Sol and Convert CO I-24-40, I-24-25, I-24-34
Item | Description - Barbara Street O&M Improvements | Cost |  | Comments / Assumptions | [9 empty] | Enter Values for Yellow Cells
1.01 | Design | 15000 |  | Smal design @10% -- Note anticipate in-house design and inspection are likely |  | 6in | 8in | 10in | 12in | 15in | 18in | 21in | 24in |  | 6in | 8in | 10in | 12in | 15in | 18in | 21in | 24in
1.02 | Environmental Design | 0 |  |  | Length: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rehab. Cost per Ft 2025 Estimate | 75 | 50 | 60 | 100 | 200 | 225 | 250 | 300
2.01 | Temporary and/or Permanent Easements | 0 |  | No easements anticipated | CCTV: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bursting Cost per Ft Estimate | 275 | 275 | 300 | 325 | 350 | 450 | 500 | 600
2.02 | Permits (ROW, VCWPD, 401, 404, etc.) | 2500 |  | Assume a $2,500 permit | Rehab (Lining): | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Dig and Replce per Ft Estimate | 450 | 500 | 550 | 600 | 700 | 800 | 1000 | 1250
3.01 | Construction Management | 8000 |  | CM assistance at 5% | Bursting: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CCTV/Prep Cost per Ft 2025 Estimate | 15 | 10 | 10 | 10 | 12 | 15 | 15 | 20
3.02 | Construction Phase Services | 8000 |  | CPS at 5% | Dig and Replace | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Avg prop line (dense) | 75
3.03 | Inspection | 21000 |  | Contract inspection for 12 days | [9 empty] | Avg prop line (rural) | 200
3.04 | Material Testing | 0 |  |  |  | 0 | [7 empty] | Sewer Lateral Re-establishment | 1500
4.01 | Restoration | 0 |  | Restoration embedded in constructon. No major restoration projects anticipated. | [9 empty] | Sewer Lateral Insert | 4000
4.02 | Mitigation | 0 |  | No mitigation anticipated | [9 empty] | Traffic Control / Day (Minor) | 1500
5.01 | Mobilization | 7000 | [11 empty] | Traffic Control / Day (Significant) | 3000
5.02 | Traffic Control | 18000 |  | Simple TC for 12 days | [9 empty] | Traffic Control / Day (Caltrans) | 3500
5.03 | Point Repairs | 127400 |  | Construct two manholes in Barbara St Area, convert 3 cleanouts | [9 empty] | Point Repair Est. | 10000
5.04 | CCTV Inspection and Pipe Preparation | 0 | [11 empty] | Point Repair High GW | 15000
5.05 | Sewer Main Lining (>6in) | 0 | [11 empty] | Inspection / Day | 1760
5.06 | Sewer Main Bursting (6in) inc. Lateral Connection | 0 | [11 empty] | Standard Manhole Construction | 25480
5.07 | Sewer Main Replacement | 0
5.08 | Sewer Lateral Re-Establishment (CIPP only) | 0
5.09 | Sewer Lateral Insert (CIPP only) | 0
6.1 | Closeout, As-builts | 1100
| TOTAL | 210000 | 0
| Design and Environmental | 17500
| Inspection and Construction Management | 37000
| Construction and Closeout | 153500
| Total Cost | 208000
1

## Redwood Bursting
Cover Sheet | Mira Monte Sewer Improvements (Redwood Tree Issue)
Item | Description - Pipe Burst 6in and relocate MH from Redwood | Cost |  | Comments / Assumptions | [9 empty] | Enter Values for Yellow Cells
1.01 | Design | 44000 |  | Small complex design @15% -- Note complex property owner coordination + evalation of adjacent buildings |  | 6in | 8in | 10in | 12in | 15in | 18in | 21in | 24in |  | 6in | 8in | 10in | 12in | 15in | 18in | 21in | 24in
1.02 | Environmental Design | 20000 |  | Anticipate need for arborist report ($10k + $10k over time) | Length: | 445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rehab. Cost per Ft 2025 Estimate | 75 | 50 | 60 | 100 | 200 | 225 | 250 | 300
2.01 | Temporary and/or Permanent Easements | 0 |  | No easements anticipated | CCTV: | 6675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bursting Cost per Ft Estimate | 275 | 275 | 300 | 325 | 350 | 450 | 500 | 600
2.02 | Permits (ROW, VCWPD, 401, 404, etc.) | 5000 |  | Private property-potentially VC or CT | Rehab (Lining): | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Dig and Replce per Ft Estimate | 450 | 500 | 550 | 600 | 700 | 800 | 1000 | 1250
3.01 | Construction Management | 11000 |  | CM assistance at 7.5% | Bursting: | 122375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CCTV/Prep Cost per Ft 2025 Estimate | 15 | 10 | 10 | 10 | 12 | 15 | 15 | 20
3.02 | Construction Phase Services | 11000 |  | CPS at 7.5% | Dig and Replace | 22500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Avg prop line (dense) | 75
3.03 | Inspection | 35000 |  | Contract inspection for 20 days | [9 empty] | Avg prop line (rural) | 200
3.04 | Material Testing | 0 |  |  |  | 445 | [7 empty] | Sewer Lateral Re-establishment | 1500
4.01 | Restoration | 50000 |  | Significant restoration to private property anticipated | [9 empty] | Sewer Lateral Insert | 4000
4.02 | Mitigation | 0 |  | No mitigation anticipated | [9 empty] | Traffic Control / Day (Minor) | 1500
5.01 | Mobilization | 11000 | [11 empty] | Traffic Control / Day (Significant) | 3000
5.02 | Traffic Control | 7000 |  | Caltrans TC for 2 days | [9 empty] | Traffic Control / Day (Caltrans) | 3500
5.03 | Point Repairs | 51000 |  | Construct two new manholes, abandon one manhole | [9 empty] | Point Repair Est. | 10000
5.04 | CCTV Inspection and Pipe Preparation | 7000 | [11 empty] | Point Repair High GW | 15000
5.05 | Sewer Main Lining (>6in) | 0 | [11 empty] | Inspection / Day | 1760
5.06 | Sewer Main Bursting (6in) inc. Lateral Connection | 122000 | [11 empty] | Standard Manhole Construction | 25480
5.07 | Sewer Main Replacement | 23000
5.08 | Sewer Lateral Re-Establishment (CIPP only) | 0
5.09 | Sewer Lateral Insert (CIPP only) | 0
6.1 | Closeout, As-builts | 3000
| TOTAL | 400000 | 0
| Design and Environmental | 69000
| Inspection and Construction Management | 57000
| Construction and Closeout | 274000
| Total Cost | 400000
| Conceptual Design | 22000
| Final Design | 45000
1 | Construction inc CM, Insp | 333000
| Total Cost | 400000

## Lomita
Cover Sheet | The scope of this project is from 2011 CIP
Item | Description - Lomita Ave. Vertical Realignment | Cost |  | Comments / Assumptions | Enter Values for Yellow Cells
1.01 | Design | 23000 |  | Complex design @ 10% (survey, Caltrans coordination) | Days | 10
1.02 | Environmental Design | 0 |  |  | Inspection | 1760
2.01 | Temporary and/or Permanent Easements | 0 |  | No easements anticipated | Bypass/day | 10000
2.02 | Permits (ROW, VCWPD, 401, 404, etc.) | 10000 |  | VCWPD and County
3.01 | Construction Management | 23000 |  | CM assistance at 10% |  | 8in
3.02 | Construction Phase Services | 12000 |  | CPS at 5% | Pipeline Construction | 650
3.03 | Inspection | 18000 |  | Contract inspection
3.04 | Material Testing | 10000 |  | Caltrans ROW. Compaction, nuclear gauge, etc. | Traffic Control / Day (Minor) | 1500
4.01 | Restoration | 0 |  | Restoration embedded in constructon. No major restoration projects anticipated. | Traffic Control / Day (Significant) | 3000
4.02 | Mitigation | 0 |  | No mitigation anticipated | Traffic Control / Day (Caltrans) | 3500
5.01 | Mobilization | 11000
5.02 | Traffic Control | 30000
5.03 | Temporary Piping & Flow Diversion | 60000 |  | Estimate 6 days of bypass inc. setup
5.04 | Pipeline Construction (200 LF) | 130000 |  | May be able to reduce this length. Need survey.
6.1 | Closeout, As-builts | 3000
| TOTAL | 330000 | 0
Note on C3: Rick Nack: Is Inspection included in this item?

## Pirie
Cover Sheet
Item | Description - Pirie Road Vertical Realignment | Cost |  | Comments / Assumptions
1.01 | Design | 25000 |  | Complex design @ 10% (survey, Caltrans coordination) | Enter Values for Yellow Cells
1.02 | Environmental Design | 0 |  |  | Days | 13
2.01 | Temporary and/or Permanent Easements | 0 |  | No easements anticipated | Inspection | 1760
2.02 | Permits (ROW, VCWPD, 401, 404, etc.) | 20000 |  | City, Caltrans, and VCWPD | Bypass/day | 10000
3.01 | Construction Management | 25000 |  | CM assistance at 10%
3.02 | Construction Phase Services | 12000 |  | CPS at 5% |  | 8in
3.03 | Inspection | 23000 |  | Contract inspection | Pipeline Construction | 650
3.04 | Material Testing | 2500
4.01 | Restoration | 0 |  | Restoration embedded in constructon. No major restoration projects anticipated. | Traffic Control / Day (Minor) | 1500
4.02 | Mitigation | 0 |  | No mitigation anticipated | Traffic Control / Day (Significant) | 3000
5.01 | Mobilization | 12000 |  |  | Traffic Control / Day (Caltrans) | 3500
5.02 | Traffic Control | 45500
5.03 | Temporary Piping & Flow Diversion | 60000 |  | Estimate 6 days of bypass inc. setup
5.04 | Pipeline Construction (200 LF) | 130000 |  | May be able to reduce this length. Need survey.
6.1 | Closeout, As-builts | 4000
| TOTAL | 360000 | 0

## Prospect
Cover Sheet
Item | Description - Prospect Meter Flume Installation and Pipeline Realignment | Cost |  |  | Enter Values for Yellow Cells
1.01 | Design | 36000
1.02 | Environmental Design | 56000 |  | Arborist report + inspection during excavation and backfill | Bypass Costs / Day | 10000
2.01 | Temporary and/or Permanent Easements | 15000 |  | Property owner | Traffic Control / Day | 750
2.02 | Permits (ROW, VCWPD, 401, 404, etc.) | 5000 |  | Parks, possibly Roads | Shoring / Day | 2000
3.01 | Construction Management | 54000 |  |  | Point Repair or Mod. (Trunk) | 10000
3.02 | Construction Phase Services | 27000 |  |  | Inspection | 1760
3.03 | Inspection | 44000
3.04 | Material Testing | 10000 |  | Compaction, pavement, pipeline | Crew Size (avg) | 5
4.01 | Restoration | 30000 |  | Anticipate some planting, fencing, etc. | Equipment (avg) | 4300
4.02 | Mitigation | 0 |  | None anticipated |  |  |  | Labor | Equipment | Materials/Disposal | Total
5.01 | Mobilization | 26000 |  |  | Site Preparation | 4 | Days | 22880 | 19780 | 5000 | 47660
5.02 | Traffic Control | 19000 |  | Maintain trail closure | Excavation | 8 | Days | 45760 | 39560 | 8000 | 93320
5.03 | Site Preparation inc. Temporary Piping & Flow Diversion | 148000 |  | Estimate 10 days bypassing | Flume Install | 2 | Days | 11440 | 9890 | 22000 | 43330
5.04 | Excavation (150 LF of 15in) | 94000 |  |  | Pipeline | 5 | Days | 28600 | 24725 | 12750 | 66075
5.05 | Flume Install | 44000 |  |  | Backfill | 2 | Days | 11440 | 9890 | 33333.3333 | 54663.3333
5.06 | Pipeline Install | 67000 |  |  | Restoration | 4 | Days | 22880 | 19780 | 15000 | 57660
5.07 | Backfill | 55000 |  |  | Total | 25 | Days
5.08 | Paving and Restoration | 58000
5.09 | SCADA I&C | 25000
6.01 | Closeout, As-builts | 5000
| TOTAL | 820000 | 0

## Foster Park
Cover Sheet
Item | Description - Foster Park Trunk Sewer Relocation | Cost |  |  | Enter Values for Yellow Cells
1.01 | Design | 187000 |  | 5% design
1.02 | Environmental Design | 187000 |  | 5% design for CEQA + arborist report + arborist |  | 8in | 10in | 12in | 15in | 18in | 21in | 24in
2.01 | Temporary and/or Permanent Easements | 50000 |  | Access through Edison Dr. property? | Drilling Cost |  |  |  | 2500 |  |  | 3000
2.02 | Permits (ROW, VCWPD, 401, 404, etc.) | 15000 |  |  | Point Repair Trunk | 15000
3.01 | Construction Management | 374000 |  |  | Point Repair Trunk Hi GW | 20000
3.02 | Construction Phase Services | 187000 |  |  | Days | 20
3.03 | Inspection | 36000 |  |  | Inspection | 1760
3.04 | Material Testing | 200000 |  |  | Traffic Control | 750 | Only for trail closure
4.01 | Restoration | 50000 |  | Planting, fencing, restoration of private property, etc.
4.02 | Mitigation | 0 |  | No mitigation anticipated (outside of waterway) |  | 8in | 10in | 12in | 15in | 18in | 21in | 24in
5.01 | Mobilization | 178000 |  |  | Drill Length: | 0 | 0 | 0 | 0 | 0 | 0 | 995
5.02 | Traffic Control | 30000 |  | Trail closure + 3 days in CT ROW for equipment/material delivery | Pipe Length | 0 | 0 | 0 | 0 | 0 | 0 | 995
5.03 | Temporary Piping & Flow Diversion | 68000 |  | 4 days set up + 3 days bypassing (only BP during tie-in)
5.04 | Select Demolition, including Piping, Fittings, Existing MHs | 40000
5.05 | Site Preparation for HDD | 25000
5.06 | HDPE Pipe (Welded) | 78000 |  | Pipe, fittings, technician (2 days)
5.07 | HDD Pipe Installation (995 ft + 50 ft each end) | 3285000
5.08 | Tie In to Collection System with Two New MHs | 40000
6.01 | Closeout, As-builts | 28000
| TOTAL | 5060000 | 0

## SAC Siphon
Cover Sheet
Item | Description - San Antonio Creek Siphon Replacement | Cost |  |  | Enter Values for Yellow Cells
1.01 | Design | 114000 |  | Complex design @ 10% - HDD
1.02 | Environmental Design | 171000 |  | Significant environmental assistance required, assume 15% construction cost |  | 8in | 10in | 12in | 15in | 18in | 21in | 24in
2.01 | Temporary and/or Permanent Easements | 50000 |  |  | Drilling Cost |  |  |  | 2500
2.02 | Permits (ROW, VCWPD, 401, 404, etc.) | 35000 |  | Permits from RB, ACOE, VCWPD, Caltrans, etc. | Point Repair Trunk | 20000
3.01 | Construction Management | 114000 |  | CM assistance at 10% | Days | 40 | insp. only
3.02 | Construction Phase Services | 57000 |  | CPS at 5% | Inspection | 1760
3.03 | Inspection | 70000 |  | Contract inspection
3.04 | Material Testing | 50000 |  | Geotechnical, pipeline |  | 8in | 10in | 12in | 15in | 18in | 21in | 24in
4.01 | Restoration | 40000 |  |  | Drill Length: | 0 | 0 | 0 | 350 | 0 | 0 | 0
4.02 | Mitigation | 103000 |  | Need to update based on impacted area - 50ftx150ft in1 location, 3:1, $200k/acre | Pipe Length | 0 | 0 | 0 | 700 | 0 | 0 | 0
5.01 | Mobilization | 57000
5.02 | Temporary Piping & Flow Diversion | 80000 |  | Limit cost by only bypassing during tie-in | TC in CT ROW | 5000
5.03 | Traffic Control | 25000 |  | Delivery/pickup of materials and equipment (5 days) - reduce by accessing from south end?
5.04 | Select Demolition, including Piping, Fittings, Existing MHs | 40000
5.05 | Site Preparation for HDD | 40000
5.06 | HDPE Pipe (Welded) | 40000 |  | Pipe, fittings, technician (2 days), update with actual ISCO HDPE pricing
5.07 | HDD Pipe Installation (250 ft + 50 ft each end) | 875000
5.08 | Tie In to Collection System with Two New MHs | 40000
6.01 | Closeout, As-builts | 17000
| TOTAL | 2020000 | 0

## Creek Siphons
Cover Sheet
Item | Description - Creek Road Siphons (4) Replacement | Cost |  |  |  | Length | Length Future | Size | Size Future | Barrels | Pipe Total | Enter Values for Yellow Cells
1.01 | Design | 234000 |  | Complex design @ 7.5% - 4x HDD designs | Stewart | 85 | 135 | 8 | 15 | 2 | 270
1.02 | Environmental Design | 468000 |  | Significant environmental assistance required, assume 15% construction cost | 10 MPH | 90 | 140 | 14 | 15 | 2 | 280 |  | 8in | 10in | 12in | 15in | 18in | 21in | 24in
2.01 | Temporary and/or Permanent Easements | 60000 |  |  | Country Club | 225 | 275 | 14 | 15 | 2 | 550 | Drilling Cost |  |  |  | 2500 | 3000
2.02 | Permits (ROW, VCWPD, 401, 404, etc.) | 100000 |  | Permits from RB, ACOE, VCWPD, Caltrans, etc. x 4 if 4 separate projects? | Hermosa | 280 | 330 | 14 | 18 | 2 | 660 | Point Repair Trunk | 15000
3.01 | Construction Management | 312000 |  | CM assistance at 10% | Total | 680 | 880 |  |  |  | 1760 | Point Repair Trunk Hi GW | 20000
3.02 | Construction Phase Services | 156000 |  | CPS at 5% | [7 empty] | Days | 80 | insp. only
3.03 | Inspection | 141000 |  | Contract inspection | [7 empty] | Inspection | 1760
3.04 | Material Testing | 200000 |  | Geotechnical, pipeline | [7 empty] | Traffic Control/Day | 2500
4.01 | Restoration | 80000
4.02 | Mitigation | 826000 |  | Need to update based on impacted area - 50ftx150ft in 8 locations, 3:1, $200k/acre | [8 empty] | 8in | 10in | 12in | 15in | 18in | 21in | 24in
5.01 | Mobilization | 156000 | [9 empty] | Drill Length: | 0 | 0 | 0 | 550 | 330 | 0 | 0
5.02 | Temporary Piping & Flow Diversion | 160000 |  | Limit cost by only bypassing during tie-in | [7 empty] | Pipe Length | 0 | 0 | 0 | 1100 | 660 | 0 | 0
5.03 | Traffic Control | 200000
5.04 | Select Demolition, including Piping, Fittings, Existing MHs | 40000
5.05 | Site Preparation for HDD | 80000
5.06 | HDPE Pipe (Welded) | 110000 |  | Pipe, fittings, technician (2 days) ea location, update with actual ISCO HDPE pricing
5.07 | HDD Pipe Installation (250 ft + 50 ft each end) | 2370000
5.08 | Tie In to Collection System with Two New MHs | 160000 |  | 4 locations
6.01 | Closeout, As-builts | 35000
| TOTAL | 5890000 | 0

## Cast and Ductile
Cover Sheet |  |  | 7
| Techite | 1829.01 | feet | CIPP: | 595902.375 | Burst: | 1348555.5 |  | Enter Values for Yellow Cells
| Line Segment | Basin | Pipe Length | Pipe Material | Pipe Size | Street Address Upstream |  |  |  | 6in | 8in | 10in | 12in | 15in | 18in | 21in | 24in
| I-19-03-I-19-04 | AO9 | 118 | TEC | 21 | 9950 OLD CREEK RD | 29500 | 70800 | Rehab. Cost per Ft 2025 Estimate | 75 | 50 | 60 | 100 | 200 | 225 | 250 | 300
| I-19-02-I-19-03 | AO9 | 143 | TEC | 21 | Old Creek Rd | 35750 | 85800 | Bursting Cost per Ft Estimate | 250 | 275 | 300 | 350 | 450 | 500 | 600 | 700
| G-19-01-G-19-03 | CO7 | 456.4 | TEC | 15 | OJAI TRAIL | 91280 | 205380 | CCTV/Prep Cost per Ft 2025 Estimate | 15 | 10 | 10 | 10 | 12 | 15 | 15 | 20
| G-19-03-G-19-04 | CO7 | 374.96 | TEC | 15 | OJAI TRAIL | 74992 | 168732 | Avg prop line (dense) | 75
| G-19-04-G-19-05 | CO7 | 386.74 | TEC | 18 | OJAI TRAIL | 87016.5 | 193370 | Avg prop line (rural) | 200
| G-19-05-G-19-06 | CO7 | 349.91 | TEC | 18 | OJAI TRAIL | 78729.75 | 174955 | Sewer Lateral Re-establishment | 1500
[9 empty] | Sewer Lateral Insert | 4000
| Cast Iron | 3347 | feet | CIPP: | 1381975 | Burst: | 2666606.25 |  | Traffic Control / Day (Minor) | 1500
| Line Segment | Basin | Pipe Length | Pipe Material | Pipe Size | Street Address Upstream |  |  | Traffic Control / Day (Significant) | 3000
| P-29-22-P-29-23 | AO6 | 123 | CIP (Cast Iron Pipe) | 8 | 517 OAK CREEK LN | 6150 | 33825 | Traffic Control / Day (Caltrans) | 3500
| P-29-23-Q-29-14 | AO6 | 326 | CIP (Cast Iron Pipe) | 12 | 517 OAK CREEK LN | 32600 | 114100 | Point Repair Est. | 10000
| N-27-01-N-27-02 | AO7 | 309 | CIP (Cast Iron Pipe) | 10 | OJAI TRAIL | 18540 | 92700 | Point Repair High GW | 15000
| O-26-02B-O-26-03B | AO8 | 140 | CIP (Cast Iron Pipe) | 14 | 11969 CREEK RD | 28000 | 63000 | Inspection / Day | 1760
| P-27-03-A-P-27-04-A | AO8 | 224 | CIP (Cast Iron Pipe) | 14 | 1720 CREEK RD | 44800 | 100800
| Q-29-14-Q-29-15 | AO8 | 246 | CIP (Cast Iron Pipe) | 12 | 539 S Ventura St | 24600 | 86100
| Q-29-16A-Q-29-17A | AO8 | 82 | CIP (Cast Iron Pipe) | 14 | 539 S VENTURA ST | 16400 | 36900 | TOTAL Cost to CIPP Minus Techite, ACP | Techite is a separate project
| Q-29-16B-Q-29-17B | AO8 | 82 | CIP (Cast Iron Pipe) | 8 | 539 S Ventura St | 4100 | 22550 | 1836475 | ACP is Dekker (Former MO trunk relocation) and Old Creek Road Rehab
| P-27-03-B-P-27-04-B | AO8 | 224 | CIP (Cast Iron Pipe) | 8 | 1720 Creek Rd | 11200 | 61600 | Higher cost than typical because non-consecutive pipe segments, near Caltrans, etc.
| O-26-02A-O-26-03A | AO8 | 140 | CIP (Cast Iron Pipe) | 10 | 11969 CREEK RD | 8400 | 42000
| J-20-01-J-20-02 | AO9 | 156 | CIP (Cast Iron Pipe) | 18 | 10200 CREEK RD | 35100 | 78000 | 638000 | Collectors
| P-30-25-P-30-24 | A10 | 16 | CIP (Cast Iron Pipe) | 12 | 302 W OJAI AVE | 1600 | 5600 | 1175000 | Trunks
| P-30-24-P-30-23 | A10 | 46 | CIP (Cast Iron Pipe) | 12 | 236 W OJAI AVE | 4600 | 16100
| N-29-02-N-29-01 | BO1 | 33 | CIP (Cast Iron Pipe) | 8 | 1401 Maricopa Hwy | 1650 | 9075
| K-26-04-K-26-05 | CO1 | 32 | CIP (Cast Iron Pipe) | 6 | 661. W. VILLANOVA RD | 2400 | 8000
| H-21-44-H-21-46 | CO5 | 151 | CIP (Cast Iron Pipe) | 8 | 99 SHORT ST | 7550 | 41525
| G-13-04-H-13-01 | DO1 | 448 | CIP (Cast Iron Pipe) | 24 | OJAI TRAIL | 134400 | 313600
| G-13-01-G-13-02 | DO1 | 443 | CIP (Cast Iron Pipe) | 24 | OJAI TRAIL | 132900 | 310100
| H-17-09-H-17-01 | DO1 | 126 | CIP (Cast Iron Pipe) | 24 | SULFUR MOUNTAIN RD | 37800 | 88200
| Ductile Iron | 808 | feet | CIPP: | 454500 | Burst: | 707000
| Line Segment | Basin | Pipe Length | Pipe Material | Pipe Size | Street Address Upstream
| J-21-15-J-21-16 | AO9 | 321 | DIP | 18 | 10300 CREEK RD | 72225 | 160500
| J-21-16-J-20-01 | AO9 | 205 | DIP | 18 | 10200 CREEK RD | 46125 | 102500
| K-22-12-K-22-13 | AO9 | 282 | DIP | 18 | 10660 Creek Rd | 63450 | 141000
| ACP | 1088 | feet | CIPP: | 348160 | Burst: | 856800
| Line Segment | Basin | Pipe Length | Pipe Material | Pipe Size | Street Address Upstream
| S-30-15-S-30-16 | AO1 | 69 | ACP | 16 | 1002 E Ojai Ave | 13800 | 31050
| S-30-11-S-30-12 | AO1 | 352 | ACP | 16 | 1180 E Ojai Ave | 70400 | 158400
| S-30-12-S-30-13 | AO1 | 120 | ACP | 16 | 1002 E Ojai Ave | 24000 | 54000
| S-30-13-S-30-15 | AO1 | 160 | ACP | 16 | 1002 E Ojai Ave | 32000 | 72000
| S-30-07-S-30-11 | AO1 | 387 | ACP | 16 | 1202 E Ojai Ave | 77400 | 174150
| Dekker Property | 2629.6 | feet
| Line Segment | Basin | Pipe Length | Pipe Material | Pipe Size | Street Address Upstream
| H-25-01-H-25-02 | BO4 | 405.2 | ACP | 18 | 578 BURNHAM RD | Pipe: | 1458040
| H-25-02-H-25-04 | BO4 | 238.7 | ACP | 21 | 2430 BURNHAM RD | New MHs: | 109566.6667
| H-25-04-H-25-06 | BO4 | 127 | ACP | 21 | 2455 BURNHAM RD | Embankment Repair: | 880000
| H-25-06-H-25-07 | BO4 | 305.7 | ACP | 21 | 2455 BURNHAM RD
| H-26-03-H-26-04 | BO4 | 356 | ACP | 21 | 410 OLD BALDWIN RD
| H-26-04-H-26-05 | BO4 | 405 | ACP | 21 | 2027 BURNHAM RD
| H-26-05-H-26-06 | BO4 | 402 | ACP | 18 | 2027 BURNHAM RD
| H-26-06-H-25-01 | BO4 | 390 | ACP | 18 | 2027 BURNHAM RD